RER615 communication settings

Ethernet rear port settings

| Parameter | Values (Range) | Unit | Step | Default | Description |
| --- | --- | --- | --- | --- | --- |
| IP address |  |  |  | 172.16.0.99 | IP address for rear port(s) |
| Subnet mask |  |  |  | 255.255.255.0 | Subnet mask for rear port(s) |
| Default gateway |  |  |  | 172.16.0.1 | Default gateway for rear port(s) |
| Mac address |  |  |  | XX-XX-XX-XX- XX-XX | Mac address for rear port(s) |

IEC 60870-5-101/104 settings

| Parameter | Values (Range) | Unit | Step | Setting | Description |
| --- | --- | --- | --- | --- | --- |
| Operation | 1=on 5=off |  |  | 1=on | Selects if this protocol instance is enabled or disabled |
| Port | 1=IEC101 - COM 1 2=IEC101 - COM 2 3=IEC104 - Ethernet |  |  | 3=IEC104 - Ethernet | Port selection |
| ClientIP |  |  |  | 172.16.0.3 | IP address of the client |
| TCP Port | 0...65535 |  | 1 | 2404 | Server TCP port |
| Start Delay | 0...20 | char | 1 | 4 | Frame start delay for serial communication |
| End Delay | 0...20 | char | 1 | 4 | Frame end delay for serial communication |
| Device Address | 1...65535 |  | 1 | 1 | Device address |
| ASDU Address | 1...65535 |  | 1 | 1 | Common address of ASDU |
| Link Mode | 0=Balanced 1=Unbalanced |  |  | 1=Unbalanced | Link mode setting |
| COT Length | 1...2 |  | 1 | 2 | Cause of transmission length |
| IOA Length | 1...3 |  | 1 | 3 | Information Object Address length |
| Link Address Length | 1...2 |  | 1 | 2 | Link Address Length |
| ASDU Address Length | 1...2 |  | 1 | 2 | ASDU Address Length |
| Single Char Resp | 0=False 1=True |  |  | 0=False | Single character response enabled/ disabled |
| Show Bad Time | 0=False 1=True |  |  | 1=True | Enable/disable bad time quality indication in events |
| Time Format | 0=Short 24bit 1=Full 56bit |  |  | 1=Full 56bit | Time stamp format 3 or 7 octet |
| Table continues on next page |  |  |  |  |  |

IEC 60870-5-101/104 settings (continues)

| Parameter | Values (Range) | Unit | Step | Setting | Description |
| --- | --- | --- | --- | --- | --- |
| Event Time | 0=Local 1=UTC |  |  | 0=Local | Selects between UTC/Local time |
| Overflow Mode | 0=Oldest +indication 1=Keep newest |  |  | 1=Keep new | Event buffer overflow handling mechanism |
| OvInd IOA | 0...16777215 |  | 1 | 60000 | Overflow indication address for interrogated data |
| OvInd NoGI IOA | 0...16777215 |  | 1 | 60000 | Overflow indication address for non- interrogated data |
| Event Order | 0=Accurate time 1=Preserve chronology |  |  | 1=Chrono | Selects the event ordering principle |
| Selection Timeout | 1...65 | s | 1 | 30 | Selection timeout for control SBO operations |
| Counter Reporting | 0=Read by master 1=Spontaneous |  |  | 0=Read by master | Counter reporting after freeze |
| Freeze mode | 0=Not in use 1=Freeze only 2=Freeze and Reset |  |  | 0=Not in use | Periodic freezing mode for integrated totals |
| TX window (k) | 1...20 |  | 1 | 12 | IEC60870-5-104 transmit window (k) |
| RX window (w) | 1...20 |  | 1 | 8 | IEC60870-5-104 receive window (w) |
| TX timeout (t1) | 1...60000 | ms | 1 | 30000 | IEC60870-5-104 transmit timeout (t1) |
| RX timeout (t2) | 1...60000 | ms | 1 | 10000 | IEC60870-5-104 receive timeout (t1) |
| Test interval (t3) | 1...60000 | ms | 1 | 20000 | IEC60870-5-104 link test interval (t3) |
| Cyclical Period | 1...604800 |  | 1 | 10 | Cyclical period in seconds |
| IT_FRZ | 0=False 1=True |  |  | 0=False | Control point for freezing integrated totals |
| Inverted DIR bit | 0=False 1=True |  |  | 0=False | Special mode for masters that require inverted DIR bit on Balanced IEC101 line. If enabled, this protocol instance will be non-compliant with the IEC 60870-5-101 standard. |